Riser Sizing for Vertical Stacked Fan Coils

As we move from refrigerant based systems to hydronic systems to transfer energy around a building, due to A2L limitations, our piping and riser system design need careful consideration especially when vertical stacked fan coils are used with factory mounted risers.  The goal is to provide adequate heating and/or cooling to all parts of the building without excessive pressure drop or noise.

There are pipe diameter limitations when using factory mounted copper risers because the risers with insulation must fit within the cabinet width and be aligned from the top of the building to the bottom regardless of the diameter or cabinet size.   Most manufacturers of factory mounted risers are limited to 3” diameter with 1” insulation in a 4-pipe reverse return system and possibly smaller diameter in a direct return system.   See Table 1, Fig. 2, and 3.

The three main considerations in riser sizing are flowrate, fluid velocity, and pressure drop.  These are all related but need to be independently calculated.

Flowrate:  GPM = BTUH/500 x delta T

Example:  20-story building with a 1-ton fan coil on each floor of the riser stack using 12F delta T chilled water:               GPM = 240,000BTUH/500x12

= 40 GPM

Velocity for Copper Pipe:  Q = A x V

Where:  Q = Flowrate, A = cross sectional area of the pipe in sq ft, V = velocity in feet per second (fps)

Fluid velocity is important to minimize noise and pipe erosion. Note: the recommended velocity for copper pipe is 2-4fps.  Factory mounted Type K, L & M copper risers are offered by most fan coil manufacturers with each having different maximum flow rates (Table 1).

Pressure Drop:  hf = f x l/D x V2 /2g

Where: hf = head loss in ft, f = Darcy friction factor, L = length of pipe, D = diameter of pipe, V = velocity (ft/s), g = 32.174ft2/s (acceleration due to gravity)

Since velocity and pressure drop are a function of the pipe diameter, we can use tables in lieu of calculating these individually (Table 1).

Table 1 Flowrate and Pressure Drop by Pipe Sizing

|  | Type L Copper |  | Type M Copper |  | Condensate |
| --- | --- | --- | --- | --- | --- |
| Pipe Size (dia – inches) | Flowrate (GPM) | PD (PSI/100ft) | Flowrate (GPM) | PD (PSI/100ft) | (Tons) |
| 0.5” | 2.9 | 5.9 | 3.2 | 5.6 | - |
| 0.75” | 6.0 | 3.9 | 6.4 | 3.7 | <20 |
| 1.0” | 10.3 | 2.8 | 10.9 | 2.7 | 21-40 |
| 1.25” | 15.7 | 2.2 | 16.3 | 2.2 | 41-90 |
| 1.50” | 22.2 | 1.8 | 22.8 | 1.8 | 91-125 |
| 2.0” | 38.6 | 1.3 | 39.5 | 1.3 | 126-250 |
| 2.5” | 59.5 | 1.0 | 61.0 | 1.0 | - |
| 3.0” | 84.9 | 0.8 | 87.0 | 0.8 | - |
| 4.0” | 149.3 | 0.6 | 151.6 | 0.6 | - |
| 5.0” | 232.7 | 0.5 | 235.8 | 0.5 | - |
| 6.0” | 334.6 | 0.4 | 338.7 | 0.4 | - |

Return Air

HWSS

HWRS

CondS

CWR

CWS

Fig. 2 Vertical Stacked Fan Coil- Back Risers (top view)

Back Risers

Vertical Stacked Fancoil

Contact Temspec or your local rep to learn more about factory mounted risers on vertical stacked fan coils.  #v-stackfancoils #riserdesign #directreturn #reversereturn